# M Bus-Protocol for Point to Point Connection

Status 23.8.2000

- This information includes the software extension V06.00. Older versions provide only a part of the parameters described.

- All the described units refer to W. If the heat meter is parameterized to J, then  all the Mbus parameters also change accordingly.

If a heat meter is addressed over a point to point connection, then the communication to the telegrams described below is simplified. Point to point connection means that only one heat meter is connected with the readout device. This requirement is always filled when the heat meter is addressed over an opto-head or over a RS232.

# Commandos, which the heat meter processes:

| Command | Data to meter | Answer from meter |
| --- | --- | --- |
| Reset heat meter ( predefined parameter list ) | 10 40 FE 3E 16 | E5 |
| Set maximum parameter list | 68 05 05 68 43 FE 51 7F 7E 8F 16 | E5 |
| Request data from heat meter | 10 4B FE 49 16 | Data frame |
| Define primary address new. ( up from V05.00 ) | See example | E5 |

The data frame which is sent from the heat meter has the following setup:

68 LL LL 68 08 FE 72 SS SS SS SS 5F 6A VR GG NN 00 00 00 (parameter list) CS 16

Information in the data frame:

| LL | The number of all bytes in the data frame minus 6. The same information is transferred twice! |
| --- | --- |
| SS SS SS SS | Serial number of the heat meter. This number is equivalent to the serial number on the name plate and is also available in the heat meter’s menu.. |
| VR | V = Version; R = Revision of the heat meter |
| GG | Meter type! GG = 04 -> heat meter with volume measurement in back flow; GG = 0C -> heat meter with volume measurement in forward flow |
| NN | Number of the read access. Is increased with each answer. |
| Parameter list | As described later |
| CS | Check sum = Sum of all the bytes in the data frame up from the fifth byte ( 08 ) to the last byte in the parameter list.. All overflows are ignored. |

The parameter list:

Each value, that can be transferred from the heat meter, is called a parameter. The sum of all the values that can be transferred from the heat meter is called a parameter list. Because the number of transferable parameters changes subject to the settings of the heat meter, the parameter list is variable. If for example, no valuation date data is available yet, because the valuation date has not yet been reached then no data on the valuation date is transferred. Also, the meters/counters of additional input units are only then transferred, when the input units are configured.

In addition to these basic versions of the parameter list, a distinction is made between a predefined parameter list and a maximum parameter list. The predefined parameter list is a list, which represents which parameter are normally transferred. The most important data for the heat meter are in this list. Which data is important for each application can be programmed in the heat meter with the corresponding software. This limited parameter list has the advantage that the one hand the data transmission can be done much quicker and on the other hand, the receiving software can be limited to the necessary parameters. The maximum parameter list contains all of the parameters for the heat meter which are available at the time.

Each parameter in the parameter list is always made up of an identifier, which is transferred first and the actual value. Using the identifier the receiver can determine which parameter is being transferred, how long the parameter is, which data coding is present and with which device the parameter is being transferred. The data are transferred by the heat meter as long as possible with maximum resolution. However, should the meter reading exceed the transferable value, then the device (identifier) is changed so that the complete value acquired by the heat meter, can be transferred. Thus it is necessary that the receiver be able to process all identifiers for a parameter.

The maximum parameter list:

| Parameter | For device | Data format | Identifier | Data ( with nibble valency ) |
| --- | --- | --- | --- | --- |
| Customer number |  | BCD6 | 0B 79 | 10 32 54 |
| Energy | Wh * 10-3 | BCD12 | 0E 00 | 10 32 54 76 98 BA |
| or | Wh * 10-2 | BCD12 | 0E 01 | 10 32 54 76 98 BA |
| or | Wh * 10-1 | BCD12 | 0E 02 | 10 32 54 76 98 BA |
| or | Wh | BCD12 | 0E 03 | 10 32 54 76 98 BA |
| or | Wh * 10 | BCD12 | 0E 04 | 10 32 54 76 98 BA |
| or | Wh * 100 | BCD12 | 0E 05 | 10 32 54 76 98 BA |
| or | kWh | BCD12 | 0E 06 | 10 32 54 76 98 BA |
| or | kWh * 10 | BCD12 | 0E 07 | 10 32 54 76 98 BA |
| Cooling energy | Wh * 10-3 | BCD12 | 4E 00 | 10 32 54 76 98 BA |
| or | Wh * 10-2 | BCD12 | 4E 01 | 10 32 54 76 98 BA |
| or | Wh * 10-1 | BCD12 | 4E 02 | 10 32 54 76 98 BA |
| or | Wh | BCD12 | 4E 03 | 10 32 54 76 98 BA |
| or | Wh * 10 | BCD12 | 4E 04 | 10 32 54 76 98 BA |
| or | Wh * 100 | BCD12 | 4E 05 | 10 32 54 76 98 BA |
| or | kWh | BCD12 | 4E 06 | 10 32 54 76 98 BA |
| or | kWh * 10 | BCD12 | 4E 07 | 10 32 54 76 98 BA |
| Volume | ml | BCD12 | 0E 10 | 10 32 54 76 98 BA |
| or | ml * 10 | BCD12 | 0E 11 | 10 32 54 76 98 BA |
| or | ml * 100 | BCD12 | 0E 12 | 10 32 54 76 98 BA |
| or | l | BCD12 | 0E 13 | 10 32 54 76 98 BA |
| or | l * 10 | BCD12 | 0E 14 | 10 32 54 76 98 BA |
| or | l * 100 | BCD12 | 0E 15 | 10 32 54 76 98 BA |
| or | m3 | BCD12 | 0E 16 | 10 32 54 76 98 BA |
| or | m3* 10 | BCD12 | 0E 17 | 10 32 54 76 98 BA |
| Additional volume 1 | ml | BCD12 | 4E 10 | 10 32 54 76 98 BA |
| or | ml * 10 | BCD12 | 4E 11 | 10 32 54 76 98 BA |
| or | ml * 100 | BCD12 | 4E 12 | 10 32 54 76 98 BA |
| or | l | BCD12 | 4E 13 | 10 32 54 76 98 BA |
| or | l * 10 | BCD12 | 4E 14 | 10 32 54 76 98 BA |
| or | l * 100 | BCD12 | 4E 15 | 10 32 54 76 98 BA |
| or | m3 | BCD12 | 4E 16 | 10 32 54 76 98 BA |
| or | m3* 10 | BCD12 | 4E 17 | 10 32 54 76 98 BA |
| Additional volume 2 | ml | BCD12 | 8E 01 10 | 10 32 54 76 98 BA |
| or | ml * 10 | BCD12 | 8E 01 11 | 10 32 54 76 98 BA |
| or | ml * 100 | BCD12 | 8E 01 12 | 10 32 54 76 98 BA |
| or | l | BCD12 | 8E 01 13 | 10 32 54 76 98 BA |
| or | l * 10 | BCD12 | 8E 01 14 | 10 32 54 76 98 BA |
| or | l * 100 | BCD12 | 8E 01 15 | 10 32 54 76 98 BA |
| or | m3 | BCD12 | 8E 01 16 | 10 32 54 76 98 BA |
| or | m3* 10 | BCD12 | 8E 01 17 | 10 32 54 76 98 BA |
| Forward-flow temperature | °C * 10-2 | INT16 | 02 59 | 10 32 |
| Back-flow temperature | °C * 10-2 | INT16 | 02 5d | 10 32 |
| Temperature difference | K * 10-2 | INT16 | 02 61 | 10 32 |
| Flow rate | l/h * 10-3 | BCD6 | 0B 38 | 10 32 54 76 流速应该都是BCD6 |
| or | l/h * 10-2 | BCD6 | 0B 39 | 10 32 54 76 |
| or | l/h * 10-1 | BCD6 | 0B 3A | 10 32 54 76 |
| or | l/h | BCD6 | 0B 3B | 10 32 54 76 |
| or | l/h * 10 | BCD6 | 0B 3C | 10 32 54 76 |
| or | l/h * 100 | BCD6 | 0B 3D | 10 32 54 76 |
| or | m3/h | BCD6 | 0B 3E | 10 32 54 76 |
| or | m3/h * 10 | BCD6 | 0B 3F | 10 32 54 76 |
| Output | W * 10-3 | BCD8 | 0C 28 | 10 32 54 76 |
| or | W * 10-2 | BCD8 | 0C 29 | 10 32 54 76 |
| or | W * 10-1 | BCD8 | 0C 2A | 10 32 54 76 |
| or | W | BCD8 | 0C 2B | 10 32 54 76 |
| or | W * 10 | BCD8 | 0C 2C | 10 32 54 76 |
| or | W * 100 | BCD8 | 0C 2D | 10 32 54 76 |
| or | kW | BCD8 | 0C 2E | 10 32 54 76 |
| or | kW * 10 | BCD8 | 0C 2F | 10 32 54 76 |
| Valuation date |  | Date | 82 04 6C | 10 32 |
| Energy at valuation date | Wh * 10-3 | BCD8 | 8C 04 00 | 10 32 54 76 |
| or | Wh * 10-2 | BCD8 | 8C 04 01 | 10 32 54 76 |
| or | Wh * 10-1 | BCD8 | 8C 04 02 | 10 32 54 76 |
| or | Wh | BCD8 | 8C 04 03 | 10 32 54 76 |
| or | Wh * 10 | BCD8 | 8C 04 04 | 10 32 54 76 |
| or | Wh * 100 | BCD8 | 8C 04 05 | 10 32 54 76 |
| or | kWh | BCD8 | 8C 04 06 | 10 32 54 76 |
| or | kWh * 10 | BCD8 | 8C 04 07 | 10 32 54 76 |
| Cooling energy at valuation date | Wh * 10-3 | BCD8 | CC 04 00 | 10 32 54 76 |
| or | Wh * 10-2 | BCD8 | CC 04 01 | 10 32 54 76 |
| or | Wh * 10-1 | BCD8 | CC 04 02 | 10 32 54 76 |
| or | Wh | BCD8 | CC 04 03 | 10 32 54 76 |
| or | Wh * 10 | BCD8 | CC 04 04 | 10 32 54 76 |
| or | Wh * 100 | BCD8 | CC 04 05 | 10 32 54 76 |
| or | kWh | BCD8 | CC 04 06 | 10 32 54 76 |
| or | kWh * 10 | BCD8 | CC 04 07 | 10 32 54 76 |
| Volume at valuation date | ml | BCD8 | 8C 04 10 | 10 32 54 76 |
| or | ml * 10 | BCD8 | 8C 04 11 | 10 32 54 76 |
| or | ml * 100 | BCD8 | 8C 04 12 | 10 32 54 76 |
| or | l | BCD8 | 8C 04 13 | 10 32 54 76 |
| or | l * 10 | BCD8 | 8C 04 14 | 10 32 54 76 |
| or | l * 100 | BCD8 | 8C 04 15 | 10 32 54 76 |
| or | m3 | BCD8 | 8C 04 16 | 10 32 54 76 |
| or | m3* 10 | BCD8 | 8C 04 17 | 10 32 54 76 |
| Additional volume 1 at valuation date | ml | BCD6 | CB 04 10 | 10 32 54 |
| or | ml * 10 | BCD6 | CB 04 11 | 10 32 54 |
| or | ml * 100 | BCD6 | CB 04 12 | 10 32 54 |
| or | l | BCD6 | CB 04 13 | 10 32 54 |
| or | l * 10 | BCD6 | CB 04 14 | 10 32 54 |
| or | l * 100 | BCD6 | CB 04 15 | 10 32 54 |
| or | m3 | BCD6 | CB 04 16 | 10 32 54 |
| or | m3* 10 | BCD6 | CB 04 17 | 10 32 54 |
| Additional volume 2 at valuation date | ml | BCD6 | 8B 05 10 | 10 32 54 |
| or | ml * 10 | BCD6 | 8B 05 11 | 10 32 54 |
| or | ml * 100 | BCD6 | 8B 05 12 | 10 32 54 |
| or | l | BCD6 | 8B 05 13 | 10 32 54 |
| or | l * 10 | BCD6 | 8B 05 14 | 10 32 54 |
| or | l * 100 | BCD6 | 8B 05 15 | 10 32 54 |
| or | m3 | BCD6 | 8B 05 16 | 10 32 54 |
| or | m3* 10 | BCD6 | 8B 05 17 | 10 32 54 |
| Performance peak 1 | W * 10-3 | BCD6 | 4B 28 | 10 32 54 |
| or | W * 10-2 | BCD6 | 4B 29 | 10 32 54 |
| or | W * 10-1 | BCD6 | 4B 2A | 10 32 54 |
| or | W | BCD6 | 4B 2B | 10 32 54 |
| or | W * 10 | BCD6 | 4B 2C | 10 32 54 |
| or | W * 100 | BCD6 | 4B 2D | 10 32 54 |
| or | kW | BCD6 | 4B 2E | 10 32 54 |
| or | kW * 10 | BCD6 | 4B 2F | 10 32 54 |
| Time of performance peak 1 |  | Date&Time | 44 6D | 10 32 54 76 |
| Performance peak 2 | W * 10-3 | BCD6 | 8B 01 28 | 10 32 54 |
| or | W * 10-2 | BCD6 | 8B 01 29 | 10 32 54 |
| or | W * 10-1 | BCD6 | 8B 01 2A | 10 32 54 |
| or | W | BCD6 | 8B 01 2B | 10 32 54 |
| or | W * 10 | BCD6 | 8B 01 2C | 10 32 54 |
| or | W * 100 | BCD6 | 8B 01 2D | 10 32 54 |
| or | kW | BCD6 | 8B 01 2E | 10 32 54 |
| or | kW * 10 | BCD6 | 8B 01 2F | 10 32 54 |
| Time of performance peak 2 |  | Date&Time | 84 01 6D | 10 32 54 76 |
| Performance peak 3 | W * 10-3 | BCD6 | 9B 01 28 | 10 32 54 |
| or | W * 10-2 | BCD6 | 9B 01 29 | 10 32 54 |
| or | W * 10-1 | BCD6 | 9B 01 2A | 10 32 54 |
| or | W | BCD6 | 9B 01 2B | 10 32 54 |
| or | W * 10 | BCD6 | 9B 01 2C | 10 32 54 |
| or | W * 100 | BCD6 | 9B 01 2D | 10 32 54 |
| or | kW | BCD6 | 9B 01 2E | 10 32 54 |
| or | kW * 10 | BCD6 | 9B 01 2F | 10 32 54 |
| Time of performance peak 3 |  | Date&Time | 94 01 6D | 10 32 54 76 |
| Date and time |  | Date&Time | 04 6D | 10 32 54 76 |
| Hours operating | h | BCD6 | 0B 26 | 10 32 54 |
| Bus address |  | INT8 | 01 7A | 10 |
| Error number |  | BCD6 | 0B FD 17 | 10 32 54 |
| Total hours of error | h | BCD6 | 8B 0C 26 | 10 32 54 |
| Error date + time |  | Date&Time | 84 0C 6D | 10 32 54 76 |
| Life of battery |  | Date | 82 08 6C | 10 32 |
| End of calibration period |  | Date | C2 08 6C | 10 32 |
| Input unit status |  | BCD8 | 0C FD 1B | 10 32 54 76 |

# Bit-coding of Date data:	YYYY.MMMM.YYYD.DDDD

Bit-coding of Date&Time data:	YYYY.MMMM.YYYD.DDDD.000H.HHHH.00mm.mmmmmm

- mmmmmm	-> minute 0..59

- HHHHH	-> hour 0..23

- DDDDD 	-> day  1..31

- MMMM 	-> month 1..12

- YYYYYYY	-> year 0..99     ( The MMMM-bits are ignored )

Bit 0 is by all representations on the right!

# Implementation instructions:

- The answer to a request can be sent with a delay of up to 500 ms. This is the minimal Timeout-time after which at the earliest a new request can be sent to the heat meter

- In certain, rare cases the heat meter cannot answer the first request. Because of this, a request which is not answered should be repeated at least three times.

- After data has been received from the heat meter, a rest period of 20 ms should be made before a new request is sent to the heat meter.

# Further information:

The complete M bus specification was written by the M bus user-group and is available for free. It can be requested as a Word-document over the internet. This document is in English and is 76 pages long.

# Example of a data request:

Transfer from readout device to heat meter:

10 4B FE 49 16	Data request

Typical answer from the heat meter:

68	Start symbol

27 27	Length of data frame minus 6 : 39 Byte ( Hex: 27 )

68 08 FE 72	Constants

10 30 33 26	Serial number of the heat meter: 26333010

5F 6A	Constants

43	Version 4 ; Revision 3

04	Device:  heat meter with volume measurement in back flow

14	Answer to the 20th data request ( Hex 14 )

00 00 00	Constants

0E 00 00 00 67 45 23 01	Energy: 12345.670000 kWh

0E 13 00 72 56 00 00 00	Volume: 567.2 m3

02 59 48 21	Forward-flow temperature: 85.2 °C ( Hex: 2148 )

02 5D E2 18	Back-flow temperature: 63.7 °C ( Hex: 18E2 )

19	Checksum

- Stop symbol

# Example: Change primary address

This switch telegram may only be used up from the version 5.00 of the heat meter. Former versions are only programmable with a more complicated program sequence.

68 06 06 68	Header

53	C field ( 73 is also possible )

FE	Accumulative address for a single device

51	CI-field for SND_UD

01 7A	primary address record

0A	desired address ( in example 10 )

27	checksum

16	End symbol

E5	Should be received as answer